## Slide 1
PO BOX 10637
CLINTON, IOWA 52732
PH: {{GC_PHONE}}9990
REV. # REV. DATE
BY
FIRST ISSUE DATE:
DESIGNED BY:
{{DESIGNED_BY}}
ER
{{ISSUE_DATE}} UPDATED WITH LATEST AHJ COMMENTS
1
{{ISSUE_DATE}}
{{PROJECT_NAME}} Club
41 Tunnel Road
{{CITY_STATE}} CA 94705 APN: 048H-7670-027
E0
COVER SHEET
BATTERY ENERGY STORAGE SYSTEM PERMIT SET
SCOPE OF WORK
THE PROJECT IS TO INSTALL NEW BATTERY ENERGY STORAGE SYSTEMS (BESS) AND
ASSOCIATED ELECTRICAL EQUIPMENT.
ALL CONSTRUCTION SHALL COMPLY WITH THE CODES ADOPTED BY CITY OF BERKELEY AS DESCRIBED IN THE OAKLAND MUNICIPAL CODE INCLUDING BUT NOT LIMITED TO 2022 CEC, CFC, CBC & CGBSC.
THE SYSTEM WILL BE INTERCONNECTED TO AND WILL BE OPERATING IN PARALLEL WITH THE ELECTRICAL UTILITY GRID PER THE REQUIREMENTS OF PASIFIC GAS AND ELECTRIC
COMPANY ({{UTILITY}}) AND THE 2022 CEC.
SITE INFORMATION | 
SITE LATITUDE | {{LAT}}, -122.242405
ZONING DISTRICT | RH-4, RU-3
FLOOD ZONE | X
EXPOSURE CATEGORY | C
SEISMIC DESIGN CATEGORY | E
COLD DESIGN TEMPERATURE [°F] | 33,8
MAX OPERATING TEMPERATURE [°F] | 84,2
S3.0
GROUNDING DETAILS FENCING DETAILS
SITE CLEARING NOTES (IF APPLICABLE)
1. PROTECT FROM DAMAGE AND PRESERVE TREES, SHRUBS, AND OTHER PLANTS OUTSIDE THE LIMITS OF WORK AND WITHIN THE LIMIT OF THE WORK WHICH ARE DESIGNATED TO REMAIN UNDISTURBED.
RECORD DRAWINGS
KEEP UP-TO-DATE AND ACCURATE A COMPLETE RECORD SET OF PRINTS FOR THE CONTRACT DRAWINGS SHOWING EVERY CHANGE FROM THE ORIGINAL DRAWINGS MADE DURING THE COURSE OF CONSTRUCTION INCLUDING FINAL LOCATION, ELEVATION, SIZES, MATERIALS, AND DESCRIPTION OF ALL WORK.
RECORDS SHALL BE "REDLINED" ON A SET OF CONSTRUCTION PLAN DRAWINGS AT THE SITE. A COMPLETE SET OF CORRECTED AND COMPLETED RECORD DRAWING PRINTS SHALL BE SUBMITTED TO OWNER PRIOR TO SUBSTANTIAL COMPLETION AT SITE.
ELECTRICAL NOTES
THE LINE AND LOAD TERMINALS ON THE DC DISCONNECTS MAY BE ENERGIZED IN THE OPEN POSITION. SWITCH IS TO BE LABELED TO COMPLY WITH ARTICLE 690.17 OF THE NEC.
BATTERY ENERGY STORAGE SYSTEM (BESS) SHALL BE CLEARLY MARKED IN ACCORDANCE WITH THE NEC LABELING REQUIREMENTS ARTICLE 690.
GROUNDING OF THE BESS SHALL COMPLY WITH NEC 690.45 AND 690.47.
THE ELECTRICAL CONTRACTOR IS REQUIRED TO USE PERMANENTLY COLOR CODED INSULATION AND PROVIDE A COLOR CODE TO IDENTIFY DC AND AC CIRCUITS AND IN ACCORDANCE WITH NEC.
IN EVERY PULL BOX, TERMINAL BOX, AND AT ALL PLACES WHERE WIRES MAY NOT BE READILY IDENTIFIED BY NAMEPLATE MARKINGS ON THE EQUIPMENT TO WHICH THEY CONNECT, IDENTIFY EACH CIRCUIT WITH A PLASTIC LABEL OR TAG FOR NUMBER, POLARITY, OR PHASE.
FLEX CONDUIT SHALL ONLY BE USED WHEN SPECIFIED OR APPROVED BY CLEARSKY.
THIS ELECTRICAL INSTALLATION IS TO BE CONSIDERED AN OPTIONAL STANDBY SYSTEM PER CEC 702.
THE GREAT POWER {{BAT_MODEL}} BATTERY STORAGE SYSTEMS ARE TO BE CONSIDERED PRE-ENGINEERED STATIONARY BATTERY STORAGE SYSTEMS.
GENERAL NOTES
ALL CONSTRUCTION SHALL COMPLY WITH THE CODES ADOPTED BY CITY OF BERKELEY AS DESCRIBED IN THE OAKLAND MUNICIPAL CODE INCLUDING BUT NOT LIMITED TO 2022 CEC, CFC & CBC.
BEFORE INITIATING ANY WORK, THE CONTRACTOR SHALL NOTIFY ENGINEER OF RECORDS OF ANY DISCREPANCIES IDENTIFIED ON EXISTING CONDITIONS, STRUCTURE, ELECTRICAL, ETC.
CONTRACTOR SHALL BE RESPONSIBLE FOR ALL SAFETY PRECAUTIONS, OSHA REQUIREMENTS AND SAFETY MEASUREMENTS ON SITE.
CONTRACTOR IS RESPONSIBLE FOR INSTALLING ALL EQUIPMENT AND FOLLOWING ALL MANUFACTURER'S OR ENGINEER'S DIRECTIONS AND INSTRUCTIONS.
CONTRACTOR IS ADVISED THAT ALL DRAWINGS, COMPONENT MANUALS, ESPECIALLY INVERTER MANUALS, ARE TO BE READ AND UNDERSTOOD PRIOR TO INSTALLATION OR ENERGIZING OF ANY EQUIPMENT.
CONTRACTOR IS RESPONSIBLE FOR SELECTING AND PURCHASING EQUIPMENT DESIGNED TO LAST A MINIMUM OF 30 YEARS IN CONJUNCTION WITH THE BESS SYSTEM. ALL ENCLOSURES, CONDUITS, STRAPS, PAINTED METAL SURFACES, CONCRETE, GROUNDING EQUIPMENT AND OTHER EQUIPMENT AND OTHER PRODUCTS SHALL BE SELECTED TO LAST THE LIFECYCLE OF THE BESS SYSTEM.
ALL CONTRACTORS ARE REQUIRED TO PROVIDE FULL SUBMITTALS OF INTENDED ORDERS TO CLEARSKY FOR REVIEW.
WHENEVER ANY SURFACE IMPROVEMENTS SUCH AS PAVEMENT, CURBING, PEDESTRIAN WALKS, FENCING, OR TURFING HAVE BEEN REMOVED, DAMAGED, OR OTHERWISE DISTURBED BY THE CONTRACTOR'S OPERATIONS; THEY SHALL BE REPAIRED OR REPLACED TO THE PRE-EXISTING CONDITION. THE REPAIRS ARE TO MEET THE OWNER'S SATISFACTION.
REFILL AND RESTORE THE WORK AS DIRECTED, DURING CONSTRUCTION AND PRIOR TO PROJECT COMPLETION, TO MAINTAIN ACCEPTABLE SURFACE CONDITIONS.
ALL ADDITIONAL MATERIALS REQUIRED SHALL BE FURNISHED WITHOUT ADDITIONAL COST TO THE OWNER.
ANY WORK BEGUN PRIOR TO ATTAINING APPROVAL AND SIGNATURES OF AHJ WILL BE AT CONTRACTOR'S RISK, AND WILL ONLY BE ALLOWED IF PRE-APPROVED BY PROJECT OWNER.
COORDINATE OPERATIONS WITH ALL REQUIRED MATERIALS TESTING SERVICES AS REQUIRED BY THESE DRAWINGS. EACH PHASE OF CONSTRUCTION SHALL BE TESTED AND APPROVED BY AHJ AS REQUIRED PRIOR TO PROCEEDING TO SUBSEQUENT PHASES.
NOTIFY ALL UTILITY COMPANIES INVOLVED IN THE DEVELOPMENT PRIOR TO BEGINNING OF WORK.
COMPLY WITH ALL CURRENTLY APPLICABLE SAFETY LAWS OF ALL JURISDICTIONAL BODIES. PROVIDE AND MAINTAIN ALL BARRICADES, SAFETY DEVICES, AND CONTROL OF TRAFFIC WITHIN AND AROUND THE CONSTRUCTION AREA. FOR ALL TRENCH EXCAVATION 5 FEET OR MORE IN DEPTH, OBTAIN PERMITS PRIOR TO BEGINNING ANY EXCAVATION.
MAINTAIN CONTINUOUS TEMPORARY TRAFFIC BARRICADES, WITH OPERABLE FLASHING DEVICES, SPACED AT INTERVALS OF NOT TO EXCEED 50 FEET WHENEVER THE WORK AREA IS ADJACENT TO AN EXISTING TRAFFIC LANE AND THERE IS A PAVEMENT CUT, TRENCH, OR DITCH WHICH IS OVER 2 INCHES IN DEPTH, OR IF THE TRAFFIC LANE USED BY VEHICLES IS NOT PAVED. IF THE CUT, TRENCH OR DITCH IS MORE THAN 10 FEET FROM A TRAFFIC LANE, THEN THE BARRICADE SPACING MAY BE GREATER, PROVIDED THAT IT DOES NOT EXCEED 200 FEET.
CONTRACTOR AGREES THAT, IN ACCORDANCE WITH GENERALLY ACCEPTED CONSTRUCTION PRACTICES, CONTRACTOR SHALL BE REQUIRED TO ASSUME SOLE AND COMPLETE RESPONSIBILITY FOR JOB SITE CONDITIONS DURING THE COURSE OF THE CONSTRUCTION OF THE PROJECT, INCLUDING SAFETY OF ALL PERSONS AND PROPERTY.
ALL PASIFIC GAS AND ELECTRIC COMPANY ({{UTILITY}})-REQUIRED EQUIPMENT SHALL BE INSTALLED IN ACCORDANCE WITH CURRENT PASIFIC GAS AND ELECTRIC COMPANY ({{UTILITY}}) STANDARDS.
ALL CONSTRUCTION AND MATERIAL DELIVERY VEHICLES SHALL USE THE DESIGNATED ACCESS AND HAUL ROUTE(S) TO THE CONSTRUCTION SITE. ANY DEVIATION IN ROUTE(S) SHALL BE SUBJECT TO OWNER'S APPROVAL. THE ROUTE(S) SHALL BE MONITORED DURING THE PROJECT FOR ANY DAMAGE AND DEBRIS ATTRIBUTABLE TO THE PROJECT VEHICLES. ALL DAMAGE AND DEBRIS AS A RESULT OF THE PROJECT SHALL BE REPAIRED TO EXISTING STANDARDS.
CONDUCT OPERATION ENTIRELY WITHIN THE PROJECT AREAS INDICATED IN THESE DRAWINGS.
WHERE ANY WORK IS BEING DONE IN AN OFF-SITE EASEMENT, NOTIFY THE PROPERTY OWNER TWO WORKING DAYS PRIOR TO COMMENCING WORK WITHIN SAID EASEMENT.
DO NOT DISPOSE OF CHLORINATED OR OTHER CHEMICALLY TREATED OR POLLUTED WATER INTO ANY DRAINAGE SYSTEM OR TO AREA SOILS.
ALL FASTNERS SHALL BE TORQUED TO THE SPECIFICATION LISTED IN THE LATEST MANUFACTURERS MANUAL OR DATASHEET. WHERE POSSIBLE ALL FASTNERS SHALL BE TORQUE MARKED USING A CLEARSKY APPROVED METHOD.
CH PROPERTY OWNER LLC 401 CONGRESS AVE STE 2750
AUSTIN,TX 78701
ELECTRICAL ENGINEER
{{EE_NAME}} BHARTIYA, ME, EE, FPE, LEED AP SACRAMENTO ENGINEERING CONSULTANTS 10555 OLD PLACERVILLE ROAD SACRAMENTO, CA 95827
{{EE_EMAIL}}
PHONE: {{EE_PHONE}} 368-4468 ext. 105
FAX: {{EE_PHONE}} 368-4490
GENERAL CONTRACTOR
BRIGHT POWER INC DBA CLEARSKY
PO BOX 10637
CLINTON, CA 52732
info@bpi-power.com PHONE: {{GC_PHONE}} 252-9990
FAX: {{GC_PHONE}} 252-9992 WWW.CLEARSKY-POWER.COM LICENSE NUMBER: 930054
LICENSE CLASSIFICATION: A, C10
STRUCTURAL ENGINEER
REX ARASHI
APPLIED ENGINEERING CONSULTANTS, INC
PROPERTY OWNER 10360 CAREY DR
GRASS VALLEY, CA 95945 {{SE_EMAIL}} PHONE: {{SE_PHONE}} 838-5358
00
01
SPECIAL INSPECTION LIST (checked items are required )
FOUNDATION
Piers and Caissons Grading and Drainage
Other
Shotcrete or Masonry Concrete Placement
Other
High Strength Bolting
Other
SEISMIC RESISTANCE
Structural Wood Structural Steel
Other
WIND RESISTANCE
STRUCTURAL OBSERVATIONS (list below )
Title 24 Energy - ECC Verification (PSR REQUIRED) Construction Formwork Certification
Special Case
CONCRETE CONSTRUCTION
F'C = 3,000 psi Reinf. Placement
Bolts in Concrete
STEEL CONSTRUCTION
Field/Shop Welding
Date:
C/MECH/PLUMB NOT CHECKED
SHEET | DESCRIPTION | REV
E0 | COVER SHEET | 00
E1.0 | PLOT PLAN | 01
E1.1 | ENLARGED PLOT PLAN | 01
CEE1.2 DEMOLITION PLAN 01 |  | 
E2.0 | SINGLE LINE DIAGRAM | 00
E3.0 | SIGNAGE | 00
S1.1 | BESS PAD DETAILS | 01
S1.2 | GEAR PAD DETAILS | 00
BESS INFO |  | BATTERY CABINET | BATTERY RACK | BATTERY INVERTER | RE
 | MANUFACTURER | GREAT POWER | GREAT POWER | By: {{INV_MFR}} | 
 | MODEL NUMBER | MAX-20HC-5000 | LIQRACK-280AH 1P416S | LLC CPS-1250 [480V] | 
 | COUNT | 1 | 12 | 1 | 
 | BATTERY BANK CAPACITY [kWh] | 5 000 | 372.7 |  | 
 | ROUND TRIP EFFICIENCY | 93.5% | N/A | 98% | 
 | VOLTAGE | 1 331.2 VDC | 1 331.2 VDC | 480 VAC | 
 | PHASE | N/A | N/A | 3 | 
 | INVERTER RATING [kVA] | N/A | N/A | 802 | 
 | WEIGHT [lbs] | 49 798 | 7054.8 | 1 980 | 
 | ENCLOSURE TYPE | IP55 | N/A | IP54 | 
 | RATED OUTPUT CURRENT | 193A (DC) | N/A | 964.6 A (AC) ELE | 
Ordinances
VISIONS NEED REVIEW
X6345
BUILDING CODE
Subject to CBC Sections 105.4, 107.3 and CRC R105.4 and R106.3
SURVEY (REVIEW ONLY) PLOT PLAN REVIEW PARKING/DRIVEWAY LAYOUT
GRADING & EROSION CONTROL SOILS REPORT ON FILE
{{CHECKED_BY}}
CHECKED BY:
EXP. 3/31/21
JOB NO.:
25-48
04/08/2026
Plan check engineer: Johnny Liu jliu2@oaklandca.gov
ALL WORK SHALL COMPLY WITH THE CBC, CRC, CPC, CMC, CEC, AND OTHER APPLICABLE CODES AS AMENDED AND ADOPTED BY THE CITY OF OAKLAND IN EFFECT AT THE TIME OF
PERMIT APPLICATION
SHEET INDEX
B2600662
REVIEWED FOR COMPLIAN
CITY OF OAKLAND BUILDING SERVICES PLAN CHECK SECTION
For Substantial Compliance With Codes anSd2.0
REMOVE OBSTRUCTIONS, TREES, SHRUBS, GRASS AND OTHER VEGETATION TO PERMIT INSTALLATION OF NEW CONSTRUCTION. REMOVAL INCLUDES DIGGING OUT STUMPS AND OBSTRUCTIONS AND GRUBBING ROOTS.
FILL DEPRESSIONS CAUSED BY CLEARING AND GRUBBING OPERATIONS WITH SOIL MATERIAL APPROVED BY OWNER, UNLESS FURTHER EXCAVATION OR EARTHWORK IS INDICATED.
STRIP TOPSOIL WHERE REQUIRED. STOCKPILE IN AREA APPROVED BY OWNER.
WITH OWNER'S APPROVAL, REMOVE EXISTING ABOVE AND BELOW GRADE IMPROVEMENTS AS INDICATED AND AS NECESSARY TO FACILITATE NEW CONSTRUCTION.
DISPOSE OF REMOVED TREES, BRUSH, STUMPS, ROOTS AND ORGANIC DEBRIS IN A LEGAL MANNER OFF THE SITE.
REVIEWED FOR COMPLIANCE SUBJECT TO FIELD INSPECTION
Oakland Fire Department Fire Prevention Bureau PCB
Oakland, CA 94612
FDPR26-00369 04.13.26 41 Tunnel Rd. - B2600362
OFD NOTES:
1.
Provide required minimum 5 feet setback with non-combustible vegetation or structure. Ref. CA Wildland Urban Interface Code.

## Slide 2
PO BOX 10637
CLINTON, IOWA 52732
PH: {{GC_PHONE}}9990
REV. # REV. DATE
BY
FIRST ISSUE DATE:
DESIGNED BY:
{{DESIGNED_BY}}
ER
{{ISSUE_DATE}} UPDATED WITH LATEST AHJ COMMENTS
1
{{ISSUE_DATE}}
{{PROJECT_NAME}} Club
41 Tunnel Road
{{CITY_STATE}} CA 94705 APN: 048H-7670-027
E1.0
PLOT PLAN
PLOT PLAN
1
E1.0
SCALE: 1'' = 50'
CLAREMONT AVENUE
DOMINGO AVENUE
APN: 048H-767-027
BESS Container
AC Disconnect 1-2
(E) Utility XFMR
AC Disconnect 1-1
ARRAY 1 POINT OF INTERCONNECTION
41 Tunnel Road, {{CITY_STATE}} 94705 2000A, 480Y/277, 3PH, 4W
37'-1"
APN: 064-4225-003
APN: 048H-7670-017-01
APN: 048H-7670-024
APN: 048H-7670-021
APN: 064-4225-005
APN: 064-4225-004
APN: 048H-7670-025
CLAREMONT AVENUE
TUNNEL ROAD
APN: 048H-7672-013
APN: 048H-7672-026
APN: 048H-7672-015
APN: 048H-7673-001
161'-9"
28'-4"
ESTIMATED TRENCHING | LENGTH (FT)
ASPHALT | 161'-9"
TOTAL | 161'-9"
SYSTEM | POI1
Inverter | 1 DYNA POWER COMPANY LLC {{INV_MODEL}} Gen5 [600V][SI1-SB] 982 kW ENERGY STORAGE INVERTER
Battery Cabinet | 1 Guangzhou Great Power Energy Storage Technology Co., Ltd {{BAT_MODEL}} ({{KWH}}kWh)
Battery Racks | 12 Guangzhou Great Power Energy Storage Technology Co., Ltd 1P416S (372.7kWh)
DC Size | 5016 kWh
AC Size | Derated to 802 kW
Label text
APN: 048H-7670-020
PARCEL LINES
BESS INVERTER 1-1
Isolation XFMR
NOTE:
REFER TO E1.1 FOR EQUIPMENT DIMMENSIONS.
1
BOLLARDS SPACED AROUND PAD (SEE E1.1 FOR SPACING)
PRIVACY FENCE
(SEE E1.1 FOR PLACEMENT)
1
150 KW UPS
By:
BUILDING CODE
Subject to CBC Sections 105.4, 107.3 and CRC R105.4 and R106.3
SURVEY (REVIEW ONLY) PLOT PLAN REVIEW PARKING/DRIVEWAY LAYOUT
GRADING & EROSION CONTROL SOILS REPORT ON FILE
Date:
ELEC/MECH/PLUMB NOT CHECKED
X6345
{{CHECKED_BY}}
CHECKED BY:
EXP. 3/31/21
JOB NO.:
25-48
04/08/2026
B2600662
REVIEWED FOR COMPLIANCE
CITY OF OAKLAND BUILDING SERVICES PLAN CHECK SECTION
For Substantial Compliance With Codes and Ordinances
REVISIONS NEED REVIEW
REVIEWED FOR COMPLIANCE SUBJECT TO FIELD INSPECTION
Oakland Fire Department Fire Prevention Bureau PCB Oakland, CA 94612
FDPR26-00369 04.13.26 41 Tunnel Rd. - B2600362
OFD NOTES:
1.
Provide required minimum 5 feet setback with non-combustible vegetation or structure. Ref. CA Wildland Urban Interface Code.

## Slide 3
PO BOX 10637
CLINTON, IOWA 52732
PH: {{GC_PHONE}}9990
REV. # REV. DATE
BY
FIRST ISSUE DATE:
DESIGNED BY:
{{DESIGNED_BY}}
ER
{{ISSUE_DATE}} UPDATED WITH LATEST AHJ COMMENTS
1
{{ISSUE_DATE}}
{{PROJECT_NAME}} Club
41 Tunnel Road
{{CITY_STATE}} CA 94705 APN: 048H-7670-027
E1.1
ENLARGED PLOT PLAN
ENLARGED PLOT PLAN
1
E1.1
SCALE: 1'' = 5'
BESS CONTAINER
BOLLARD (TYP.) IN ACCORDANCE WITH
CFC 2022, 1207.11.7.3 (1) SEE S1.1 FOR DIMENSIONS
8'-0"
19'-10"
1000KVA XFMR
7'-1"
5'-5"
5'-1"
1200A AC DISCONNECT
3'-0"
EQUIPMENT SETBACK FROM PROPERTY LINE
BESS PAD
(REFER TO S1.2 FOR DETAILS)
5'-0" (TYP.)
CLAREMONT AVENUE
10'-6"
11'-3"
FENCE SETBACK FROM PROPERTY LINE
DYNA POWER COMPANY LLC CPS-1250
BATTERY INVERTER
ELECTRICAL EQUIPMENT PAD (REFER TO S1.1 FOR DETAILS)
2'-11"
4'-0" (TYP.)
3'-7"
22'-9"
PARCEL LINE
PRIVACY FENCE BLOCKING VIEW FROM CLAREMONT AVENUE (ON TOP OF EQUIPMENT & BESS FOUNDATIONS) (REFER TO S3.0 FOR FENCE DETAILS)
 | BATTERY CABINET | BATTERY RACK | BATTERY INVERTER
MANUFACTURER | GREAT POWER | GREAT POWER | {{INV_MFR}}
MODEL NUMBER
MAX-20HC-5000
LIQRACK-280AH 1P416S
LLC CPS-1250 [480V]
COUNT
1
12
1
BATTERY BANK CAPACITY [kWh]
5 000
372.7
ROUND TRIP EFFICIENCY
93.5%
N/A
98%
VOLTAGE
1 331.2 VDC
1 331.2 VDC
480 VAC
PHASE
N/A
N/A
3
INVERTER RATING [kVA]
N/A
N/A
802
WEIGHT [lbs]
49 798
7054.8
1 980
ENCLOSURE TYPE
IP55
N/A
IP54
RATED OUTPUT CURRENT
193A (DC)
N/A
964.6 A (AC)
BESS INFO
3'-0" (TYP.)
8'-2"
CONTAINER DIMENSIONS IN ACCORDANCE TO CFC 2022, 1207.5.6 (TYP.)
1
1
3"
SPACING IN ACCORDANCE WITH
CFC 2022, 1207.11.7.3 (1)
1
2'-4" (TYP)
LEGEND
SYMBOL | DESCRIPTION | TOTAL
 | BOLLARDS | 11
2025 CFC 312 shall apply - typ.
{{CHECKED_BY}}
CHECKED BY:
EXP. 3/31/21
JOB NO.:
25-48
REVIEWED FOR COMPLIANCE SUBJECT TO FIELD INSPECTION
Oakland Fire Department Fire Prevention Bureau PCB Oakland, CA 94612
FDPR26-00369 04.13.26 41 Tunnel Rd. - B2600362
OFD NOTES:
1.
Provide required minimum 5 feet setback with non-combustible vegetation or structure. Ref. CA Wildland Urban Interface Code.

## Slide 4
25-48
.J:OB
06B3O7PXO A81 CLINTON,
70P7H):-252-9990
REV.
REEV.
BY
UEFIRST
DATE:
DESIGNED
CHECKED
{{DESIGNED_BY}}
{{CHECKED_BY}}
ER
{{ISSUE_DATE}} UPDATED
1
{{ISSUE_DATE}}
aPrNemont
u4n1nel {{CITY_STATE}}
HA-7P6N7:0-027
31E/X2P1.
E1.2
DEMOLITION
ENLARGED
1
E1.1
SCALE:
CLAREMONT
LEGEND |  | 
SYMBOL | DESCRIPTION | TOTAL
 | TREES/BUSHES | 1
 | MTRPSEE | 2
FTIRLEE (TTROIMMED
NTKREE
12'-4"
STUMTRPEE
EN(HAS
8'-3"
1
REVIEWED FOR COMPLIANCE SUBJECT TO FIELD INSPECTION
Oakland Fire Department Fire Prevention Bureau PCB Oakland, CA 94612
FDPR26-00369 04.13.26 41 Tunnel Rd. - B2600362
OFD NOTES:
1.
Provide required minimum 5 feet setback with non-combustible vegetation or structure. Ref. CA Wildland Urban Interface Code.

## Slide 5
2000A
INTERCONNECTION iAscConnect OPONINNETCTION Terhters mSiantgicle raAsrngde determined ED1RYNA Photovoltaic aAnzlal rdous INVERTER OlaNb-eEleledc:trical IEEE-929-2000 G1uangzhou systems 2MSA1XR-82-0AH0C1-)5000 vtehreter STORAGE u1a2ngzhou aIpfplicable, PRODUCERS RIQRACK-280AH-1P416S inverters CAUSE exclusively NORMAL U9A6NGZHOU eRnetsfer IESFINED LIQRACK-280AH-1P52S RPOEDWER ESRYSSTEM WITHOUT S)T.ORAGE bMeer:ter AINRKING ELIENCTRICAL wn(Nge)r PT BE0EMkS(WNS)h) 0V1000KVA Y/217270V0,A, Y/217270V0,A, {{KW}}kW ISOLATION AWIC,3PH, AWIC,3PH, [480V] TRANSFORMER 3R, NEMA 1, NEMA HA(BEI)ONARD 5000kWh NON-FUSED ES12(030)A 27070V0,A, BESS + _ A6 193A 964.6A 964.6A 964.6A 964.6A TIMONAIN N CADBCLE N CAABCLE AABCLE N CAABCLE N CAABCLE BATTERY EBRATTERY METER ISACONNECT ISACONNECT SECTION M Grounding XoFfMRside CONTROL 75(NA) 8IA0(NRV)Y LUL.G PANELOAD 0Y/220707AV, SECTION TAODS DISTRIBUTION XBILEITASOSRY SECTION N CAABCLE (HVAC) 100A 50(N) ... N CAABCLE ITASOSRY 50A N CAABCLE SUPPRESSION) INCOMING TFYROM N CAABCLE 10A EMS TESRITNEET N CAABCLE Apparent ltMagaex ngRtuhn oLlt-Lage Phases c. Neutral Material Current mpaTcaibtyle atiOngCP Number Voltage itCode Specification Ground Conduit [%V] D A] power %] drop [ft] ] Needed [#] Runs limit Moinr . Size 1 ADBCLE 802,0 1,56 20 1300 1 dullNyot VnCAL 193,0 301,56 350 2 1#2 4/0 4/0 1# 1-1/2 0,02 REVIEWED FOR COMPLIANCE AABCLE 802,0 1,25 5 480 3 dullNyot VnCAL 964,6 1205,82 1200 4 1#0 cm5i0l 0 kcm5i0l 0 kcm3i5l 0 3-1/2 0,01 SUBJECT TO FIELD INSPECTION Oakland Fire Department AABCLE 802,0 1,25 5 480 3 dullNyot VnCAL 964,6 1205,82 1200 4 1#0 cm5i0l 0 kcm5i0l 0 kcm3i5l 0 3-1/2 0,01 Fire Prevention Bureau PCB AABCLE 802,0 1,25 160 480 3 dullNyot VnCAL 964,6 1205,82 1200 4 kcm2i5l 0 cm5i0l 0 kcm5i0l 0 kcm3i5l 0 3-1/2 0,59 Oakland, CA 94612 FDPR26-00369 04.13.26 AABCLE 802,0 1,25 10 480 3 RateFdully TCU 964,6 1205,82 1200 4 1#0 cm3i5l 0 kcm3i5l 0 4/0 3 0,03 41 Tunnel Rd. - B2600362 AABCLE 145,4 1,25 10 480 3 RateFdully MnATL 174,0 218,75 225 1 8# cm3i0l 0 kcm3i0l 0 2# 2-1/2 0,04 OFD NOTES: AABCLE 145,4 1,25 10 480 3 RateFdully MnATL 174,0 218,75 225 1 8# cm3i0l 0 kcm3i0l 0 2# 2-1/2 0,04 1. AABCLE 83,1 1,25 160 480 3 RateFdully MnATL 100,0 125,00 125 1 1/0 2/0 2/0 4# 2 0,92 Provide required minimum 5 feet setback with non-combustible vegetation or structure. Ref. AABCLE 41,5 1,25 160 480 3 RateFdully MnATL 50,0 62,50 70 1 3# 3# 3# 6# 1-1/4 1,15 CA Wildland Urban Interface Code. AABCLE 5,0 1,25 10 480 3 RateFdully MnATL 6,0 7,51 15 1 1#2 6# 6# 6# 1 0,01 31E/X2P1. | ER |  |  |  |  |  |  |  |  |  | BY
 | UPDATED |  |  |  |  |  |  |  |  |  | 
 | {{ISSUE_DATE}} |  |  |  |  |  |  |  |  |  | REEV.
 | 1 |  |  |  |  |  |  |  |  |  | REV.
 |  |  |  |  |  |  | 06B3O7PXO A81 NAPA, 70P7H):-252-9990 |  |  |  | 
 | aPrNemont u4n1nel {{CITY_STATE}} HA-7P6N7:0-027 |  |  |  |  |  |  |  |  |  | 
 | E2.0 POIS1LD |  |  |  |  |  |  |  |  |  | 
 | UEFIRST DATE: |  |  |  |  | {{ISSUE_DATE}} |  |  |  |  | 
 | DESIGNED |  |  |  |  | {{DESIGNED_BY}} |  |  |  |  | 
 | CHECKED |  |  |  |  | {{CHECKED_BY}} |  |  |  |  | 
 | .J:OB |  |  |  |  | 25-48 |  |  |  |  | 

## Slide 6
PO BOX 10637
CLINTON, IOWA 52732
PH: {{GC_PHONE}}9990
REV. # REV. DATE
BY
FIRST ISSUE DATE:
ER
{{ISSUE_DATE}} UPDATED WITH LATEST AHJ COMMENTS
1
{{ISSUE_DATE}}
{{PROJECT_NAME}} Club
41 Tunnel Road
{{CITY_STATE}} CA 94705 APN: 048H-7670-027
CAUTION:
THIS SERVICE SUPPLIED BY ALTERNATIVE POWER SOURCES WITH DISCONNECTS LOCATED AS SHOWN
E4.0
POI1 SIGNAGE
TRUE NORTH
10"
10"
LOCATION:
BESS
QUANTITY:
1
TEXT:
HEADER: 34 point (0.472")
SUB: 18 points (0.25")
BODY: 12 points (0.167")
LOCATION:
MSB
QUANTITY:
1
TEXT:
HEADER: 34 point (0.472")
SUB: 18 points (0.25")
BODY: 12 points (0.167")
ENERGY STORAGE SYSTEM | 2"
5" | 
LOCATION:
BESS ENCLOSURE
QUANTITY:
1
TEXT:
28 point (0.281")
LOCATION:
QUANTITY:
TEXT:
LITHIUM IRON PHOSPHATE TECHNOLOGY | 2"
5" | 
ENERGY STORAGE SYSTEM DISCONNECT | 3"
5" | 
LOCATION: BESS ENCLOSURE ({{INV_MFR}})
QUANTITY:
1
TEXT:
36 point (0.359")
ENERGY STORAGE SYSTEM INVERTER | 3"
5" | 
CAUTION:
THIS SERVICE SUPPLIED BY ALTERNATIVE POWER SOURCES WITH DISCONNECTS LOCATED AS SHOWN
10"
10"
BESS Container
Isolation XFMR
& AC Disconnect 1-2
(E) Utility XFMR
AC Disconnect 1-1
ARRAY 1 POINT OF INTERCONNECTION
41 Tunnel Road, {{CITY_STATE}} 94705 2000A, 480Y/277, 3PH, 4W
41 Tunnel Road
{{CITY_STATE}}, 94705
BESS ENCLOSURE | 1 | 36 point (0.359") | LOCATION: | QUANTITY: | TEXT: | LOCATION: | QUANTITY: | TEXT:
(GREAT POWER) |  |  | BESS ENCLOSURE | 1 | 36 point (0.359") | BOLTSWITCH CABINET | 2 | 20 point (0.203")
AC DISCONNECT BOLTSWITCH CABINET OPERATING CURRENT: 1200A OPERATING VOLTAGE: 480V | 2"
5" | 
LOCATION: | QUANTITY: | TEXT:
XFMR | 1 | 20 point (0.203")
ISOLATION XFMR XFMR SIZE: 1000KVA OPERATING VOLTAGE: 480/480V | 2"
5" | 
YOU
ARE
HERE
TRUE NORTH
41 Tunnel Road
{{CITY_STATE}}, 94705
BESS Inverter 1-1
BESS Container
Isolation XFMR
& AC Disconnect 1-2
(E) Utility XFMR
AC Disconnect 1-1
ARRAY 1 POINT OF INTERCONNECTION
41 Tunnel Road, {{CITY_STATE}} 94705 2000A, 480Y/277, 3PH, 4W
YOU
ARE
HERE
BESS Inverter 1-1
REVIEWED FOR COMPLIANCE SUBJECT TO FIELD INSPECTION
Oakland Fire Department Fire Prevention Bureau PCB Oakland, CA 94612
FDPR26-00369 04.13.26 41 Tunnel Rd. - B2600362
{{DESIGNED_BY}}
DESIGNED BY:
{{CHECKED_BY}}
CHECKED BY:
EXP. 3/31/21
JOB NO.:
25-48
OFD NOTES:
1.
Provide required minimum 5 feet setback with non-combustible vegetation or structure. Ref. CA Wildland Urban Interface Code.

## Slide 7
PO BOX 10637
CLINTON, IOWA 52732
PH: {{GC_PHONE}}9990
REV. # REV. DATE
BY
FIRST ISSUE DATE:
ER
{{ISSUE_DATE}} UPDATED WITH LATEST AHJ COMMENTS
1
{{ISSUE_DATE}}
{{PROJECT_NAME}} Club
41 Tunnel Road
{{CITY_STATE}} CA 94705 APN: 048H-7670-027
S1.1
BESS Pad Detail
BESS PAD DETAILS - TOP VIEW
1
S1.1
SCALE: 1" = 2'
BESS PAD DETAILS - SIDE VIEW
2
S1.1
SCALE: 1" = 2'
BESS CONTAINER FOOTPRINT
MAINTENANCE ACCESS & FIRE CLEARANCE PER CFC 1207.1-1207.9
BATTERY TRAY ACCESS SIDE
GRADE
5'-5"
3'-8"
3'-8"
3'-7"
26'-6"
16'-6"
2'-4"
1'-0" EMBEDMENT
6"
2'-10" EMBEDMENT
4°
GRADE
SIMPSON PAB8H W/ 9" EMBEDMENT
GRAVEL BACKFILL UNDER SLAB, COMPACT WITH VIBRATORY
COMPACTOR IN 6" LIFTS
12" THICK SLAB WITH #4 BAR AT 18" O.C. EACH WAY AT TOP AND BOTTOM
1'-0"
1'-0"
#4 BAR AT 9" O.C. VERTICAL AND HORIZONTAL
BEND VERTICAL BARS INTO SLAB BY 12" MINIMUM
STANDARD HOOK AT BOTTOM
COLD JOINTS
Great Power Energy {{BAT_MODEL}} BESS
Max Wt = 86000 lbs
 | FOR PAGES PV0.2 & PV0.3
 | GENERAL NOTES: STEM WALL SECTIONS WILL NEED TO BE FORMED AND POURED FIRST WITH A COLD JOINT WITH EXTENDED VERTICAL BARS TO TIE INTO THE SLAB. GRAVEL BACKFILL WILL FOLLOW AFTER THE STEM WALLS ARE SET. THE SLAB WILL BE PLACED AFTER THE BACKFILL.
 | Design Criteria: 2025 CBC, ASCE 7-22, ACI 318-19, ANSI/AWC NDS - 2024 Risk Category 1 Wind speed = 87 mph, Exposure B Seismic Design Category D, Sds = 1.8 Soils capacities per IBC Chapter 18: Bearing = 1500 psf, lateral bearing = 200 pcf for drilled piers Concrete Notes: Use fc' = 3000 psi Use A615, Grade 60 rebar Break test are required at 7, 14 and 28 days Max w/c = 0.5 Engineering Notes: Installation of post-installed anchors (wedge anchors, epoxy anchors) require continuous special inspection. Install anchors in strict accordance with manufacturer's recommendations. Remove all top soil under perimeter of equipment pads. Compact native soil or remove any loose materials.
1'-0"
8'-0"
BESS CONTAINER
36" MIN.
48" MAX.
15" MIN.
3" MIN.
36" MIN.
48" MAX.
CONCRETE FILLED TO TOP OF
BOLLARD
CONCRETE
TYPICAL 4" BOLLARD
3
S1.1
SCALE: 1" : 1'
84" POST
10"
BOLLARD NOTES:
BOLLARDS IN REGULATION WITH CFC 312.2
REGULAR 84" POST - SCHEDULE 40 GALVANIZED STEEL PIPE.
DETAIL CONSIDERED MINIMUM FOR INSTALLATION. CARE WILL BE TAKEN TO CONFORM TO EXISTING BOLLARD AESTHETIC SUCH AS COLOR, END-CAP, OR REFLECTIVE VISIBILITY STRIPS.
REPAIRS, IF NECESSARY, SHALL BE MADE TO EXISTING FINISH GRADE AFTER BOLLARD INSTALLATION.
FINISH GRADE
3" SCHEDULE 80 STEEL PIPE
(IN ACCORDANCE TO CFC 2022, 1207.11.7.3(1))
1
SIMPSON PAB8H W/ 9" EMBEDMENT
2"
3"
14" DIAMETER x 4'-6" LONG PIER, TYP.
WOOD POSTS IN PIERS, RESTRAINED BY PAD
1
1
1
1
{{ISSUE_DATE}}, 1:10:52 PM
By:
BUILDING CODE
Subject to CBC Sections 105.4, 107.3 and
CRC R105.4 and R106.3
SURVEY (REVIEW ONLY) PLOT PLAN REVIEW PARKING/DRIVEWAY LAYOUT
GRADING & EROSION CONTROL SOILS REPORT ON FILE
Date:
ELEC/MECH/PLUMB NOT CHECKED
REVIEWED FOR COMPLIANCE
CITY OF OAKLAND BUILDING SERVICES PLAN CHECK SECTION
For Substantial Compliance With Codes and Ordinances
REVISIONS NEED REVIEW
X6345
04/08/2026
B2600662
verify 4" minimum
required. 2025 CFC
312.
{{DESIGNED_BY}}
DESIGNED BY:
{{CHECKED_BY}}
CHECKED BY:
EXP. 3/31/21
JOB NO.:
25-48
2025 CFC 312 shall apply - typ.
REVIEWED FOR COMPLIANCE SUBJECT TO FIELD INSPECTION
Oakland Fire Department Fire Prevention Bureau PCB Oakland, CA 94612
FDPR26-00369 04.13.26 41 Tunnel Rd. - B2600362
OFD NOTES:
1.
Provide required minimum 5 feet setback with non-combustible vegetation or structure. Ref. CA Wildland Urban Interface Code.

## Slide 8
PO BOX 10637
CLINTON, IOWA 52732
PH: {{GC_PHONE}}9990
REV. # REV. DATE
BY
FIRST ISSUE DATE:
DESIGNED BY:
{{DESIGNED_BY}}
ER
{{ISSUE_DATE}} UPDATED WITH LATEST AHJ COMMENTS
1
{{ISSUE_DATE}}
{{PROJECT_NAME}} Club
41 Tunnel Road
{{CITY_STATE}} CA 94705 APN: 048H-7670-027
S1.2
Gear Pad DETAILS
GEAR PAD DETAILS - TOP VIEW
1
S1.2
SCALE: 1" = 1'
GEAR PAD DETAILS - FRONT VIEW
2
(4) 3/4" SIMPSON STRONG-BOLT 2 SS
W/ 4" EMBEDMENT (TYP.)
BATTERY INVERTER FOOTPRINT
TRANSFORMER FOOTPRINT
AC DISCONNECT FOOTPRINT
1'-2"
1'-11"
1'-0"
1'-9"
4'-1"
1"
10"
10"
1'-7"
20'-1"
Maddox 1000kVA XFMR
Max Wt = 8530 lbs
Dyna Power CPS-1250 Battery Inverter
Max Wt = 1980 lbs
1200A Disconnect
Max Wt = 710 lbs
9" THICK SLAB WITH #4 BAR AT 12" O.C. EACH WAY AT MID-DEPTH
1'-0"
#4 BAR AT 9" O.C. VERTICAL AND HORIZONTAL
STANDARD HOOK AT BOTTOM
4°
1'-0"
2'-4"
6'-0"
GRADE
6"
11"
1'-6" EMBEDMENT
COLD JOINTS
BEND VERTICAL BARS INTO SLAB BY 12" MINIMUM
GRAVEL BACKFILL UNDER SLAB, COMPACT WITH VIBRATORY COMPACTOR IN 6" LIFTS
6'-11"
6'-1"
5'-6"
1'-10" EMBEDMENT
9"
GRADE
GEAR PAD DETAILS - SIDE VIEW
3
3/4" SIMPSON STRONG-BOLT 2 SS W/ 4" EMBEDMENT
7'-5"
(4) 3/8" SIMPSON STONG-BOLT 2 SS W/ 2"
EMBEDMENT (TYP.)
(4) 3/4" SIMPSON STRONG-BOLT 2 SS
W/ 4" EMBEDMENT (TYP.)
6'-3" OC MAX WOOD POST SPACING
4'-6" DEEP
3'-0" DEEP
14" DIAMETER
WOOD POST
14" DIAMETER
PIER ELEVATION
4
S1.2
SCALE: 1" = 2'
PIER PLAN VIEW
5
S1.2
SCALE: 1" = 2'
14" DIAMETER x 4'-6" LONG PIER, TYP.
WOOD POSTS IN PIERS, RESTRAINED BY PAD
1
1
1
1
1
1
1
1
6X6 PTDF WOOD POSTS
RATED FOR GROUND CONTACT
CONCRETE PAD
6" MIN
{{ISSUE_DATE}}, 1:10:52 PM
By:
BUILDING CODE
Subject to CBC Sections 105.4, 107.3 and CRC R105.4 and R106.3
SURVEY (REVIEW ONLY) PLOT PLAN REVIEW PARKING/DRIVEWAY LAYOUT
GRADING & EROSION CONTROL SOILS REPORT ON FILE
Date:
ELEC/MECH/PLUMB NOT CHECKED
REVIEWED FOR COMPLIANCE
CITY OF OAKLAND
BUILDING SERVICES
PLAN CHECK SECTION
For Substantial Compliance With Codes and Ordinances
REVISIONS NEED REVIEW
X6345
S1.2
S1.2
SCALE: 1" = 1'
SCALE: 1" = 1'
{{CHECKED_BY}}
CHECKED BY:
EXP. 3/31/21
JOB NO.:
25-48
04/08/2026
B2600662
REVIEWED FOR COMPLIANCE SUBJECT TO FIELD INSPECTION
Oakland Fire Department Fire Prevention Bureau PCB Oakland, CA 94612
FDPR26-00369 04.13.26 41 Tunnel Rd. - B2600362
OFD NOTES:
1.
Provide required minimum 5 feet setback with non-combustible vegetation or structure. Ref. CA Wildland Urban Interface Code.

## Slide 9
XFMR/ GREAT POWER GROUNDING ELECTRODE CONDUCTOR XFMR/ GREAT POWER GROUND TERMINAL NOTES: GROUNDING CLAMP SIZE OF CONDUCTORS SHALL COMPLY WITH CEC 250.94 5/8"Ø x 8'-0" LONG COPPER CLAD GROUND ROD OR OTHER ELECTRODE BOND TO SEPARATE CONDUCTORS FROM INVERTER TO METAL BUILDING FRAME AS SPECIFIED BY CEC 250.52 IF POSSIBLE (CEC 250.68) CONCRETE FOUNDATION PAD INSTALLED WITHIN STUB-UP AREA GROUND TO METAL WATER PIPE EMBEDDED AT LEAST 10'-0" INTO THE SOIL IF SEE SHEETS S1.1 FOR LOCATION AVAILABLE (CEC 250.68) GRADE CHECK RESISTANCE TO GROUND. IF RESISTANCE EXCEEDS 25 OHMS, INSTALL ADDITIONAL GROUND RODS WITH CONDUCTORS AS SHOWN SEPARATED AT LEAST 6'-0" UNTIL RESISTANCE IS REDUCED TO 25 OHMS OR LESS (CEC 250.52). PROVIDE THIRD PARTY GROUND RESISTANCE TEST. PROVIDE GAS AND WATER BOND (IF APPLICABLE). 1 GROUNDING ELECTRODE DETAIL: XFMR/ BESS/ INVERER S2.0 SCALE: NTS REVIEWED FOR COMPLIANCE SUBJECT TO FIELD INSPECTION Oakland Fire Department Fire Prevention Bureau PCB Oakland, CA 94612 FDPR26-00369 04.13.26 2 DIAGRAM OF GROUNDING POINTS 41 Tunnel Rd. - B2600362 S2.0 SCALE: NTS OFD NOTES: 1. Provide required minimum 5 feet setback with non-combustible vegetation or structure. Ref. CA Wildland Urban Interface Code. EXP. 3/31/21 | ER |  |  |  |  |  |  |  |  |  | BY
 | UPDATED WITH LATEST AHJ COMMENTS |  |  |  |  |  |  |  |  |  | 
 | {{ISSUE_DATE}} |  |  |  |  |  |  |  |  |  | REV. DATE
 | 1 |  |  |  |  |  |  |  |  |  | REV. #
 |  |  |  |  |  |  | PO BOX 10637 CLINTON, IOWA 52732 PH: {{GC_PHONE}}9990 |  |  |  | 
 | {{PROJECT_NAME}} Club 41 Tunnel Road {{CITY_STATE}} CA 94705 APN: 048H-7670-027 |  |  |  |  |  |  |  |  |  | 
 | S2.0 GROUNDING DETAIL |  |  |  |  |  |  |  |  |  | 
 | FIRST ISSUE DATE: |  |  |  |  | {{ISSUE_DATE}} |  |  |  |  | 
 | DESIGNED BY: |  |  |  |  | {{DESIGNED_BY}} |  |  |  |  | 
 | CHECKED BY: |  |  |  |  | {{CHECKED_BY}} |  |  |  |  | 
 | JOB NO.: |  |  |  |  | 25-48 |  |  |  |  | 

## Slide 10
25-48
JOB NO.:
PO BOX 10637
CLINTON, IOWA 52732
PH: {{GC_PHONE}}9990
REV. # REV. DATE
BY
FIRST ISSUE DATE:
DESIGNED BY:
CHECKED BY:
{{DESIGNED_BY}}
{{CHECKED_BY}}
ER
{{ISSUE_DATE}} UPDATED WITH LATEST AHJ COMMENTS
1
{{ISSUE_DATE}}
{{PROJECT_NAME}} Club
41 Tunnel Road
{{CITY_STATE}} CA 94705 APN: 048H-7670-027
EXP. 3/31/21
S3.0
FENCING DETAIL
FENCING DETAILS - ISOMETRIC VIEW
1
S3.0
SCALE: NTS
FENCING DETAILS - PARKING LOT VIEW
2
S3.0
SCALE: NTS
FENCING DETAILS - CLAREMONT AVE. STREET VIEW
3
S3.0
SCALE: NTS
8'-0"
8'-0"
BESS CONTAINER
1000KVA XFMR
1200A AC DISCONNECT
DYNA POWER COMPANY LLC CPS-1250 BATTERY INVERTER
6X6 PTDF WOOD POSTS RATED FOR GROUND CONTACT PAINTED
TO MATCH SHEETING
6'-3" OC MAX WOOD POST SPACING
8' HIGH PRIVACY FENCE
(ON TOP OF EQUIPMENT & BESS FOUNDATIONS)
26 GAUGE MBCI PBR WALL PANEL, OR SIMILAR, 8', TAN PAINTED,#987665
1
1'-0"
1'-0"
.
TOP AND BOTTOM RAILS (2x4 FLAT OR 2x4 STACKED)
SIMPSON FB24Z BRACKET W/HZ10 COATING, TYP.
1'-0"
1'-0"
SIMPSON FB24Z BRACKET W/HZ10 COATING, TYP.
6'-3" OC MAX WOOD POST SPACING
1'-0"
1'-0"
8'-0"
{{ISSUE_DATE}}, 1:10:52 PM
By:
BUILDING CODE
Subject to CBC Sections 105.4, 107.3 and CRC R105.4 and R106.3
SURVEY (REVIEW ONLY) PLOT PLAN REVIEW PARKING/DRIVEWAY LAYOUT
GRADING & EROSION CONTROL SOILS REPORT ON FILE
Date:
ELEC/MECH/PLUMB NOT CHECKED
X6345
04/08/2026
B2600662
REVIEWED FOR COMPLIANCE
CITY OF OAKLAND BUILDING SERVICES PLAN CHECK SECTION
For Substantial Compliance With Codes and Ordinances
REVISIONS NEED REVIEW
REVIEWED FOR COMPLIANCE SUBJECT TO FIELD INSPECTION
Oakland Fire Department Fire Prevention Bureau PCB Oakland, CA 94612
FDPR26-00369 04.13.26 41 Tunnel Rd. - B2600362
OFD NOTES:
1.
Provide required minimum 5 feet setback with non-combustible vegetation or structure. Ref. CA Wildland Urban Interface Code.